## Assumptions
Nouaceur DC peak-shaving — BESS vs Transmission upgrade
Inputs and assumptions ¦ Source: BloombergNEF 2025 BESS Cost Survey, ONEE/EIB-KfW, World Bank MENA HV benchmarks, ACWA/MASEN Noor Midelt II/III auction
Parameter | Value | Unit | Note
SIZING
IT load (Nouaceur DC) | 500 | MW | First-article sizing
Target grid connection (post-shave) | 350 | MW | Stated objective
Peak shaved by BESS | 150 | MW | 500 – 350
BESS power | 50 | MW | Co-located
BESS energy | 200 | MWh | 4-hr equivalent
BESS UNIT COSTS
BNEF 2025 global avg installed cost | 110 | $/kWh | BloombergNEF 2025
Hardware cost (= 200 MWh × $110/kWh) | 22 | $M | Computed
Morocco premium low | 28 | $M | Import duty, EPC, WACC 7-9%
Morocco premium high | 32 | $M | Import duty, EPC, WACC 7-9%
TRANSMISSION UNIT COSTS
Reinforcement size low | 100 | MW | Casablanca southern ring
Reinforcement size high | 150 | MW | Casablanca southern ring
Capex per MW low | 1 | $M/MW | World Bank MENA HV
Capex per MW high | 2 | $M/MW | World Bank MENA HV
Total capex low | 100 | $M | 100 MW × $1M/MW
Total capex high | 300 | $M | 150 MW × $2M/MW
REFERENCE BENCHMARKS ($/MWh)
BNEF global LCOS, 4-hr standalone | 78 | $/MWh | BloombergNEF 2025
Noor Midelt II — PV+BESS PPA | 32.5 | $/MWh | ACWA Power / MASEN, Aug 2025
Noor Midelt III — PV+BESS PPA | 36.5 | $/MWh | ACWA Power / MASEN, Aug 2025

## Comparison
BESS vs Transmission — capex and $/peak-MW
Option | Capex low ($M) | Capex high ($M) | $/peak-MW low ($k/MW) | $/peak-MW high ($k/MW)
BESS (200 MWh / 50 MW) | 28 | 32 | 187 | 213
Transmission upgrade (100–150 MW) | 100 | 300 | 1000 | 2000
Cost gap ($/peak-MW) | ≈ 5–11× | Transmission $/MW ÷ BESS $/MW
BESS capex: $110/kWh BNEF 2025 global avg × 200 MWh = $22M hardware; $28–32M reflects Morocco import duty on Li cells, EPC margin, WACC 7–9% (vs 4–5% EU). Transmission capex: $1–2M/peak-MW (World Bank MENA HV benchmark; cross-checked vs ONEE/EIB-KfW 2024 €300M for 730 km package).